## Slide 1: Component Design Basis Inspection (CDBI)
Graydon Strong
6/17/14

## Slide 2: CDBI Bases
This inspection of component design bases verifies that plant components are maintained within their design basis. Additionally, this inspection provides monitoring of the capability of the selected components and operator actions to perform their design bases functions. As plants age, modifications may alter or disable important design features making the design bases difficult to determine or obsolete. The plant risk assessment model assumes the capability of safety systems and components to perform their intended safety function successfully. This inspectable area verifies aspects of the Initiating Events, Mitigating Systems and Barrier Integrity cornerstones for which there are no indicators to measure performance.

## Slide 3: CDBI Objective
To gain reasonable assurance that risk significant structures, systems, and components (SSCs) can adequately perform their design basis function. This includes reasonable assurance that the risk significant component can fulfill their design basis function during or after licensee’s activities (e.g., maintenance, surveillance) which can affect component’s availability, reliability and capability. Additionally, this includes that reasonable assurance that risk significant issues resulting from the generic communications have been adequately addressed.

## Slide 4: CDBI Scope
Review 15-25 risk significant samples in Components and Operating Experience
Component Selection
  Risk-Significant Systems
  Risk-Significant/Low Margin
  Event Scenario-Based (Accident sequences)
OE actions resolved?
  Procedures updated? Mods implemented?

## Slide 5: NRC Resources
408 hours effort (+/- 15%)
Team leader
Two or three regional inspectors
  Operations/Maintenance
  Engineering
Two contractor design specialists
  Mechanical
  Electrical/I&C

## Slide 6: CDBI Implications
Every issue is a challenge to Configuration Management and Design Basis
Operability may be in question
Resources to recover from inspection

## Slide 7: Industry Violations (non minor) Since 2012
181 Violations (mostly Green NCV’s)
81 Electrical
80 Mechanical
3 Civil

## Slide 8: CDBI Violation Components
16 Relays
14 Valves
12 Pumps
11 Circuit Breakers
10 Batteries
6 Motors
5 Thermal Overloads
3 MOVs

## Slide 9: CDBI Violation Systems
22 Emergency Diesel Generators
5 DC (10 more for batteries)
4 Standby Service Water
4 DG Fuel Oil
3 Spray Ponds

## Slide 10: CDBI Violation Subjects
26 Degraded Voltage
9 HVAC
6 NPSH (Net Positive Suction Head)
6 SBO (Station Blackout)
5 PM (Preventative Maintenance)
5 Harmonics

## Slide 11: CDBI Violation Subjects
4 Time Critical Operator Actions
4 HELB (High Energy Line Break)
3 Flooding
3 Tornado
3 Uncertainties
3 Leakage

## Slide 12: CDBI Violation Processes
32 Procedures
21 Testing
19 Calculations
9 Design Basis
6 Operability

## Slide 13: Columbia Inspection Trends
5 Calculation
3 Procedure
3 PM frequency change justifications
3 50.59
2 Design Basis Knowledge

## Slide 14
Columbia Inspection Trends
50.59
Design Basis Knowledge
Calculations
PM’s

## Slide 15: 50.59
Legacy Doc Change Only 50.59s vulnerable
Sample of 80 legacy 50.59s reviewed by Industry Expert
9 were deemed either required or may require prior NRC approval (based on limited info)
Expanded sample for Industry Expert deemed not necessary

## Slide 16: Calculations
CDBI had 3 calculation related specific issues
CDBI issue with locating some calculations
  Short term: Internal audit performed
  Long term: Scan calculations
Vulnerability for the future with outstanding CMR’s and certain calculations
  Prioritized plan for CMR incorporation
  DC calculations being revised
Presented calculation plan to NRC Resident
  4 year plan to upgrade calculations

## Slide 17: PM’s
PM extensions without proper justifications
New design data base document that requires detailed references and justifications for PM changes
Vendor input, Regulatory position, and OE sections
Training for System Engineers
5 PM related procedures enhanced

## Slide 18: Design Basis Knowledge
Engineering staff needs review on design basis concepts
January 2014 ESP training performed on “Design Basis Refresher”
Periodic design basis refresher training

## Slide 19: Major Modifications
Lack of Analysis to show coordination between Non-1E and 1E loads off 1E inverters
Design modifications to move Non-1E loads off 1E inverters
Division 2
  Design for next outage installation issued
Division 1
  Design for following outage installation in progress

## Slide 20: Inverter Power Panel 8A-A

## Slide 21: CDBI Preparation
CDBI Self Assessment with internal multi discipline team and outside guests
Review of Violations from other plants
Get vulnerabilities into corrective action process and take action

## Slide 22: CDBI Support
Dedicated technically capable staff to communicate and follow issues to completion
Ensure accuracy and timeliness
If in house technical support is lacking in an area, consider outside expert
Violations addressed immediately in the Corrective Action process

## Slide 23
Questions?