## Slide 1: NFPA 805 and CONFIGURATION MANAGEMENT jim lechner June 7, 2016

## Slide 2: Configuration management
The Actual Physical Configuration of SSCs
  What the plant really looks like
The Facility Configuration Information
  What the drawings, specifications and other documentation says
The Design Requirements
  What needs to be there
  (What the NRC Thinks is there)
How does that apply to Fire Protection?
“three ball model”

## Slide 3: What is our job as configuration managers?
Appendix R has a relatively small scope of SSCs and design requirements.
  Typically ECCS and Onsite Power/Support Systems and some administrative controls
NFPA 805 requires a much larger scope of SSCs, design requirements and programmatic elements to demonstrate compliance.
  Fire PRA credits most possible ways to get “water in the pot” and any available Power/Support systems along with numerous administrative controls
Keeping the documentation aligned with the plant and the license requirements

## Slide 4: Configuration control scope

## Slide 5: Documentation Concerns
Scope
FPRA Assumptions
  Fire Modeling Zones of Influence (how they are derived)
  Credit is taken for Operating Procedures and How Operators “Respond”
  Very tight reliability and availability values of FP Systems
Programmatic Elements
  Credit is taken for Administrative Controls (i.e. transient combustibles)
  Fire Brigade Performance
NFPA Code Conformance
  Surveillance Requirements and Acceptance Criteria defined
Safe Shutdown SSCs, Circuit Analysis, and Assumptions
  Spurious Operations Combinations and Probabilities
  Non-Power Operations concerns

## Slide 6: Documentation Concerns CONT.
Radioactive Release
  Engineered features like floor drains and HVAC credited
  Storage limits imposed on contaminated materials
  Fire Brigade Training
System Performance
  MAPP runs etc. to define specific system response to events
  Timelines developed
  Onsite/Offsite Power credit
  Availability of Instrument Air
  Etc.

## Slide 7: Configuration Change process
Point of Entry
Fire Protection is Part of Applicability Determination Process
  When is 10 CFR 50.48 the “YES” Answer for Licensing Process?
Appendix R concerned with no adverse impact to safe shutdown.
  Very few License Amendments using 10 CFR 50.48
NFPA 805 concerned with increases in Fire Risk
  Easier to get to “YES” 10 CFR 50.48 is applicable process
Under NFPA 805 the Process is called Change Evaluation
  FAQ 12-061 to NEI 04-002

## Slide 8: Change evaluation process

## Slide 9: Responsibilities
Design Engineers and other “Originators” of Changes
  Use of FP Impact Screening Process to provide initial assessment of FP Licensing Basis “touchpoints”
Fire Protection Program Owners
  FP Systems and Programmatic Elements
Safe Shutdown (NSCA) Engineers
  NSCA/Safe Shutdown Databases and Analyses
FPRA Practitioners
  Fire Modeling
  Qualitative Risk Evaluations
  Quantification
Regulatory Affairs
  License Amendments

## Slide 10: What does GOOD look Like?
Understood by Fire Protection Program Owner at Site
Repeatable by Site Engineers
In a format that explains any assumptions made
Provides documented basis for decisions
Good Documentation

## Slide 11: Lessons Learned
NFPA 805 Not Resource Neutral
  Higher burden on FP analytical staff
FPRA Now Part of License Basis
  PRA No longer beyond design basis and exempt from QA, etc.
Culture Change Required from all staff
  Recognition of the many ways to change the plant
  Much lower threshold for FP License to be impacted
  Not all Fire Locations created equally

## Slide 12: Conclusion
Documentation of process is KEY
  Comprehensive Lists of Supporting Analyses
    Detailed listing of Assumptions
  Fire Protection DBD Document of License Bases
    How do you comply area by area?
Having Good Tools
  Databases and Software Tools
  FPRA Scenario Drawings
    Ignition Sources
    Fuel Packages
    Target Sets (Equipment, Cables and Raceways)

## Slide 13: QUESTIONS?
Contact
Jim Lechner
+1 402 672-0503
jlechner@jensenhughes.com
For More Information Visit
www.jensenhughes.com