## Slide 1
Revised 1/4/11
CM Equilibrium
CM Equilibrium for NNPPs
Equilibrium Upsets
CM Process Model & Equilibrium Restoration
Using CM to protect Design and Operating Margins
An Individual’s CM Responsibilities
Configuration Management Fundamentals

## Slide 2: What is CM?
In its simplest terms Configuration Management (CM) is what we do to assure ourselves and our regulators that we are doing everything we said we would do.
The objective of CM is the conformance of the three elements represented by the CM Equilibrium Model
The following slides provide an explanation of the three elements in the CM Equilibrium Model.
Design Require-ments
Facility Config Info
Physical Config
1

## Slide 3
Требования к проекту
Что должно туда входить
Данные по конфигурации объекта
Что там имеется
Физическая станция
Что там имеется на самом деле
Рабочие процессы должны обеспечивать:
Постоянное соответствие элементов
Авторизацию всех изменений
Проверку соответствия
Рабочие процессы должны обеспечивать:
Постоянное соответствие элементов
Авторизацию всех изменений
Проверку соответствия
Вот идея, которая сводит это все воедино:
Каждый из этих пунктов представляет важную концепцию!
“Трехэлементная диаграмма”
speaking the same language... in any language
Slide from presentation in Russia
What is CM Equilibrium?
2
Notes: Slide from presentation in Russian in March 2001
Same slide used in US to train on the Objective of Configuration Management
Finish with a joke: “Does anybody want me to read this for them?”

## Slide 4
What is CM Equilibrium?
Slide from presentation in China
speaking the same language... in any language
3
Notes: Slide from presentation in Russian in March 2001
Same slide used in US to train on the Objective of Configuration Management
Finish with a joke: “Does anybody want me to read this for them?”

## Slide 5: CM Equilibrium
Technical requirements, derived from the design process, that are reflected in the final design.
What Needs to be there
Design characteristics and parameters needed for the facility to perform its function
Requirements come from a number of sources; NRC regulations, OSHA, state laws, management direction, design preferences, etc.
Must be verified or monitored to confirm that design is valid
Design Requirements
Design Require-ments
4

## Slide 6: CM Equilibrium
Documentation that defines how the plant is designed and how it is operated.
What we say is there
Design Output Documents; drawings, specs, calcs, databases, test plans, etc.
Operational Configuration Documents; system alignment checklists, lockout & tagout forms
Other Operating, Maintenance, Training and Procurement Information; corrective & preventive maintenance, calibration procedures, lesson plans, safeguards SSC information, etc.
Facility Configuration Information
Facility Config Info

## Slide 7: CM Equilibrium
Actual physical location, arrangement and material condition of Structures, Systems and Components (SSCs)
SSCs as installed (design configuration)
Component position (operating configuration)
SSCs include a component’s electrical, chemical, and mechanical properties, liquids & coatings, and computer hardware & software
What is actually there
Physical Configuration
Physical Config
6

## Slide 8: CM Equilibrium
Work Processes must assure that:
Elements conform all the time
Processes are in place to restore CM Equilibrium if upset
All Changes are Evaluated and Approved
People are trained and qualified
Equilibrium conformance can be verified
Design Require-ments
Facility Config Info
Physical Config
7

## Slide 9: CM Equilibrium
Work Processes are the administrative and management measures used to ensure the configuration is maintained. These processes include;
design control
document control
work management
surveillance & test programs
work protection isolation
formal training
assessments
Design Require-ments
Facility Config Info
Physical Config
8

## Slide 10: CM Equilibrium for NNPPs
Design Require-ments
Facility Config Info
Physical Config
A computer-based information model environment formed by computer technology consisting of 2D (dimensional), 3D, 4D (time), 5D (cost), 6D (material) modeling other intelligent technologies along with data, databases, and electronic document sources.
Virtual Plant
9

## Slide 11
CM Equilibrium Upsets
Upsets are discrepancies found between any one of the three elements or they may be intentional desired changes
The following slides provide further explanations and examples
Design Require-ments
Facility Config Info
Physical Config
10

## Slide 12
CM Equilibrium Upset Examples
Maintenance opens a pump for repair and finds the configuration different than shown in vendor manual or tries to install a part drawn from Stores that will not fit
Operations goes to open a valve and finds it already open
Engineering walks down a system prior to developing a modification and finds a configuration different than shown on drawings
A data discrepancy is found between the electronic equipment database and the hard copy drawing
Chemistry wants to change the pH of water in a system from its design value
11

## Slide 13
Upsets Between Design Requirements & Facility Configuration Information
Errors in analysis, design inputs
Errors in licensing documents
Operating procedure invalidates design calculation (response time)
Desired changes, such as system improvements or technology upgrades
The following slide provides examples of this type of CM Equilibrium Upset.
Design Require-ments
Facility Config Info
CM Equilibrium Upsets
12

## Slide 14
Examples
Performance test doesn’t measure all relevant component parameters
Safety Analysis assumes system can be considered operable provided operator checks the component once per shift. Operations cost-cutting move changed rounds to once per day.
A modification is installed that puts in a new design pump, but affected preventive maintenance plans were not updated
Management commits to a later code edition and the requirements don’t get flowed down to all required documents
CM Equilibrium Upsets
Design Require-ments
Facility Config Info
13

## Slide 15
Upsets Between Physical Config & Facility Configuration Information
The most common CM Equilibrium Upset
Drawing to plant discrepancies
Components found in wrong position
“Midnight Mods”
Maintenance errors that affect plant configuration
Vendor Manual out of date
Upsets must be evaluated to determine which condition is correct
Desired changes: modifications, equivalency evaluations, changing component positions
Facility Config Info
Physical Config
CM Equilibrium Upsets
14

## Slide 16
Upsets Between Design Requirements & Physical Configuration
Construction error
Failure of SSC to meet design performance criteria
Equipment exceeds allowable tolerances
Unexpected degradation in SSC performance
The following slide provides examples of this type of CM Equilibrium Upset.
CM Equilibrium Upsets
Design Require-ments
Physical Config
15

## Slide 17
Examples
Incorrect wiring termination from construction that did not affect pre-operational or startup test results
Inadequate equivalency evaluation
Design calculation assumes that an operator can reach a valve to manually close it in 10 minutes. A seismic upgrade included a new load-bearing wall that creates a significant barrier (i.e., increased time to close the valve).
Erosion or corrosion of piping systems exceeds design margin
Design Require-ments
Physical Config
CM Equilibrium Upsets
16

## Slide 18: CM Equilibrium Restoration
The following slides present a high level model using integrated processes to return CM Upsets to the Equilibrium
The question protocol addresses the 3 CM elements
The model was developed by CMBG and has influenced the content of numerous industry guidance documents
It provides a useful tool for developing CM Performance Indicators
17

## Slide 19: CM Equilibrium Restoration
CM Equilibrium
SSCs performing as expected
People are being trained
Procedures are in place and being followed
CM Program is being monitored/trended
Evaluate Identified Problem or Desired Change
Change Facility
Configuration Information ?
Change Design
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Design
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
18
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 20: CM Equilibrium Restoration
Implementing Documents
It is recommended that facilities using this CM Fundamentals module tailor it to their specific situation. For example, after each of the upcoming slides, it would be helpful to list the site specific documents or procedures in place to implement the required actions to restore the CM Equilibrium.
For this section, there may be a CM Program Description, Policy Statement or high level procedure
Procedures governing design control, document control, work control, etc. would be appropriate
CM Equilibrium
19
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 21: CM Equilibrium Restoration
Evaluate Identified Problem or Desired Change
Apparent discrepancy (discovered error)
Unsatisfactory test results
Desired change (modification, Equivalency Evaluation, manipulating SSCs)
Evaluate Identified Problem or Desired Change
Change Design
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Design
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
20
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 22: CM Equilibrium Restoration
Implementing Documents
Evaluate Identified Problem or Desired Change
Evaluate Identified Problem or Desired Change
For this section, it would be appropriate to identify the facility’s Corrective Action Program, Self Assessment Program, System Health Monitoring Program, Periodic Test and Surveillance programs, etc.
21
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 23: CM Equilibrium Restoration
Change Design Requirements?
What are the Design Requirements?
Does identified or desired change affect Requirements?
Use Design Requirements Change process
Evaluate Identified Problem or Desired Change
Change Design
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Design
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
22
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 24: CM Equilibrium Restoration
Implementing Documents
Change Design Requirements
For this section, it would be appropriate to identify the 10CFR50.59 Process (or equivalent), Design Control Procedure, SAR Revision or License Amendment Procedure, etc.
Also be aware that Facility Configuration Information changes may need to be made
Design
Requirements Change Process
23
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 25: CM Equilibrium Restoration
Change Physical Configuration?
Modify components or change position of components?
Use Mod process or equivalency to change Configuration
Use operating procedures to change component position
Evaluate Identified Problem or Desired Change
Change Design
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Design
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
24
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 26: CM Equilibrium Restoration
Implementing Documents
Physical Configuration Change Authorization Process
For this section, it would be appropriate to identify the Modification Procedure, Work Control Procedure, Conduct of Operations Procedure, etc.
Also be aware that Facility Configuration Information changes may also need to be made
Physical Configuration Change Authorization Process
25
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 27: CM Equilibrium Restoration
Change Facility Configuration Information?
Design Output documents (drawings, calcs, specs, etc.)
Operational configuration documents
Other operating, maintenance, training, etc. documents
“The job is not complete until the paperwork is done”
Evaluate Identified Problem or Desired Change
Change Design
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Design
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
26
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 28: CM Equilibrium Restoration
Implementing Documents
Facility Configuration Information Change Process
This is probably the lengthiest list to identify
For this section, it would be appropriate to identify the drawing update procedure, procedure update procedure, database update procedure, SAR update procedure, maintenance procedure on documenting work package completion, etc.
Facility Configuration
Information Change Process
27
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 29: CM Equilibrium Restoration
Do Nothing More
If cost effective, do nothing more…except
Document your conclusion!
Evaluate Identified Problem or Desired Change
Change Design
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Design
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
28
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 30: CM Equilibrium Restoration
Implementing Documents
Do Nothing More
For this section, it would be appropriate to identify the Corrective Action Program, operability and engineering evaluation procedure, etc.
Also be aware that Facility Configuration Information changes may also need to be made
Do Nothing More
29
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 31
The following slides present a discussion of what is meant by Margin
Design margin which provides additional conservatism for some degradation issues and unanticipated conditions.
We have the range of normal operations which we should not allow to become too tight for our operators
Operating margin which addresses normal events and events of moderate frequency
Using CM to Protect
Design and Operating Margins
30

## Slide 32
Margin Definition
31
Conservatism included in operational limits and the design of every SSC in a Nuclear Facility. In quantitative terms, margin is the difference between the actual (or predicted) and required performance of a SSC. This conservatism may also be present in analyses for an entire safety function.
Margins in plant design and operational configuration ensure that technical and regulatory requirements are met and ensure consistency with design bases.
The documented limits for design requirements and operational configuration are protected by using sufficient margins to ensure consistency with the design/licensing basis.
Margin accounts for normal wear and aging of equipment, as well as uncertainties related to instrumentation and analysis methods.
Margin provides a cushion of robust design for unanticipated equipment degradation or degradation of analysis assumptions.
Margin is a safety factor included in design and analyses.

## Slide 33: CM Equilibrium  Margins
Protect the Design Basis
Design Basis
Each boundary has margins to protect these limits
Design Configuration
Operational Configuration
Operational Configuration conforms to Design Configuration
Design Configuration conforms to Design Basis
32

## Slide 34: Margins
Range of Normal Operation
Ultimate Capability
Operating Margin
Design Margin
Analyzed Design Limit
Operating Limit
Analytical Margin
Documented on design documents
Documented in engineering calculation
Failure Point Undetermined depends on many variables
controlled by Operations
controlled by Engineering
unanalyzed region
Notes on Model
describes one parameter only; different parameters may be interrelated
direction may be positive or negative
doesn’t represent all possible limits and setpoints
gaps not intended to represent relative size of margins – may be zero
33

## Slide 35: Margins
Range of Normal Operation
Ultimate Capability
Operating Margin
Design Margin
Analyzed Design Limit
Operating Limit
Analytical Margin
Documented on design documents
Documented in engineering calculation
Failure Point Undetermined depends on many variables
controlled by Operations
controlled by Engineering
unanalyzed region
Other Limits and Setpoints
Operator Alarm (HI-HI)
Operator Alarm (HI)
Tech Spec Limit
Regulatory Limit
34

## Slide 36: Margins
Operating Margin
Design Margin
Analytical Margin
Range of Normal Operation
Ultimate Capability
Analyzed Design Limit
Operating Limit
Elevator Example
Rated Load posted in elevator = 3500 lbs
Dept of Labor - design for 25% passenger overload 4375 lbs
Analyzed & tested to 4650 lbs
100 – 600 lbs
Failure Point – undetermined depends on many variables
35

## Slide 37: Margins
Normal Operation
Operating Margin
Design Margin
Analytical Margin
HVAC Example
OAC Room Temperature
Original analysis:
Room temperature must be kept under 90° F to protect computers Note: vendor’s Operating Limit = utility’s Ultimate Capability
Analyzed Design Limit = 84° F, calculated for worst case conditions
Operating Limit =78° F to give operators time to take action (analysis assumption)
High Alarm is set at 75° F (warning of abnormal condition)
84° F
78° F
72° F
75° F
90° F
36
Notes: Air conditioning unit on the roof of the Aux Bldg cools the room with the Operator Aid Computer
manufacturer says that computers must be kept at less than 90 degrees F
Our analysis shows a maximum room temperature of 84 degrees under worst case conditions (Analyzed Design Limit)
Operating Limit is 78 degrees - Operations has to take action (High Alarm goes off at 75 to give them time to take action
Normal operating range is less than 72 degrees

## Slide 38: Margins
HVAC Example
Over time margin is lost due to one or more of these causes:
heat loads added to room
lake temperature higher than analyzed
poor heat exchanger performance due to fouling
OAC Room Temperature
Normal Operation
Operating Margin
Analytical Margin
88° F
82° F
74° F
78° F
90° F
Design Margin
New Analyzed Design Limit (88°F) reduces Analytical Margin and
affects Operating Limit (78° to 82°)
affects Operating Margin
affects Alarm Setpoint (75° to 78°)
37
Notes: Over time things happen that impact the margin
Has your plant every experienced these?
other heat loads are added to room
we experience lake temperatures higher than we assumed in original analysis
raw water is hurting performance of heat exchanges more that we had assumed.
Normal operating range goes to 74 degrees
We run the calculations again using new inputs and the Analyzed Design Limit goes up to 88 degree
We get frequent nuisance alarms at 75 degrees, so we raise the Alarm Setpoint to 78
We raise the Operating Limit to 82 to allow time for operator action
Analytical Margin is now only 2 degrees = Vendors Limit (90F) – Analyzed Design Limit (88)
A new larger Air Conditioning Unit will provide greater cooling capacity

## Slide 39: Margins
Normal Operation
Operating Margin
Design Margin
Analytical Margin
OAC Room Temperature
84° F
78° F
72° F
75° F
90° F
Larger air conditioning unit can restore room temperature margin but will
require more electrical power
increase weight on Aux Building roof
HVAC Example
Voltage Analysis
Roof Structural Analysis
Normal Operation
Operating Margin
Design Margin
Analytical Margin
Normal Operation
Operating Margin
Design Margin
Analytical Margin
…resulting in other margin losses
38
Notes: Bigger air conditioning unit results in
more power, which reduces available margin on breaker
increased weight on roof decreases available structural margin of roof.

## Slide 40
39
An Individual’s CM Responsibilities
Performing routine activities in a manner to achieve CM Program objectives and principles to ensure the synchronization of plant design basis and current licensing basis requirements with plant documentation and the physical plant.
Ensuring that changes made to configuration documents are reflected in other affected documents.
Identifying configuration discrepancies through established processes.
Providing missing information found/developed during research to the appropriate data owner for verification and entry.
Notes: Bigger air conditioning unit results in
more power, which reduces available margin on breaker
increased weight on roof decreases available structural margin of roof.

## Slide 41
“It’s what you do now
When you don’t have to do anything
That let’s you be
What you want to be
When it’s too late to do anything
about it.”
Warren Owen, former Exec. VP Duke Power
40

## Slide 42
Вопросы?
Kérdések?
Otázka?
питатння?
Întrebări?
Postavljanje vprašanj?
Klausimai?
Bыnpocu
Pyetje?
Questions?
¿Pregunta?
问题
문제
Հարց
सवाल
سوالات
Notes: This slide show or slightly different earlier versions have been presented at IAEA workshops in Korea, China, Russia, Ukraine, Czech Republic, Hungary and Argentina. “Questions” has been translate into language of those who have attended . Translations may not be accurate.
  Pyetje? Albanian
  Հարց Armenian “haags”
  Bыnpocu Bulgarian “vŭpros”
  问题 Chinese “Wèntí”
  Otázka? Czech
  Kérdések? Hungarian
  सवाल Indian (Hindi) “Selbat”
  문제 Korean “munje”
  Klausimai? Lithuanian “klausimas”
  سوالات Pakistan (Urdu)
  Întrebări? Romanian “intrabaree”
  Вопросы? Russian “vopros”
  Postavljanje vprašanj? Slovenian
  ¿Pregunta? Spanish
  Питатння? Ukrainian “pytannya”