## Slide 1: Configuration Management Fundamentals
Presented By: Jon Sears
CMBG Steering Committee

## Slide 2: A Brief History of CM in the Nuclear Industry
Configuration Management in military and aerospace industry geared towards product conformance to facilitate interchangeability of parts while still satisfying the overall design requirements
MIL-STD-973 (1992), ”Configuration Management” (later replaced by ANSI/EIA-649-1998)
Notes: First couple of slides are focused on U.S. government CM initiatives
Military CM started in the post WWII era of jet aircraft development.
Many contractors and parts manufactures involved.
Rapidly evolving designs.

## Slide 3: A Brief History of CM in the Nuclear Industry
Nuclear plants in mid 60’s to early 80’s typically designed by AEs under contract
Final design documents typically turned over to the utility at the end of construction
Little knowledge transfer of design info to utility engineering organization
Utilities struggled to deal with long term design maintenance and related document upkeep
Notes: Commercial nuclear power
Not much structure – Get the documents and dump them into Records
Anyone in the audience under the age of 35. Probably never seen a “Velum Drawing”

## Slide 4: A Brief History of CM in the Nuclear Industry
Early indicators that the nuclear plant design basis knowledge was becoming disconnected from the physical plant
IE Bulletin 79-14 uncovered
  calculation discrepancies
  undocumented modifications
  document discrepancies
  as-built problems
Notes: A series of commercial nuclear industry events led to regulatory actions.
IE- NRC Inspection and Enforcement bulletins are predecessors to Generic Letters
IE Bulletin 79-14 was focused on hangers/pipe supports

## Slide 5: A Brief History of CM in the Nuclear Industry
TMI Accident (1979)
Three Mile Island accident was a partial core melt down that occurred on March 28, 1979 in one of the two TMI nuclear reactors.
Stuck open relief valve
Human Factors items and operator training
Design indicator deficiencies
INPO formed 9 months later.
Notes: The accident began with failures in the non-nuclear secondary system, followed by a stuck-open relief valve in the primary system, which allowed large amounts of coolant to escape. The mechanical failures were compounded by the initial failure of plant operators to recognize the situation as a Loss of coolant accident (LOCA) due to inadequate training and human factors such as human computer interface, design oversights relating to ambiguous control room indicators in the power plant
Industry Changes Increase Safety Within nine months of the accident, the industry had formed INPO, whose mission is to promote the highest levels of safety and reliability in the operation of nuclear power plants.

## Slide 6: A Brief History of CM in the Nuclear Industry
Salem ATWS event (1983)
Generic implications identified in NUREG-1000 and NRC Generic Letter 83-28
  compliance with vendor recommendations
  part and procurement issues
  vendor manual controls
Industry initiatives by INPO, NUMARC and EPRI to provide guidance and consistency
Notes: Salem event – Feb 1983 SG low low level event and there was no trip.
Happened twice in a couple of weeks.
Challenged the Reactor Protection System.

## Slide 7: A Brief History of CM in the Nuclear Industry
Davis Besse Loss of Feedwater event (1985)
Led to NRC Safety System Functional Inspections (SSFIs) and NUREG-1154
  difficulties maintaining operational readiness of safety systems
  lack of understanding design bases
Voluntary design basis reconstitution, DBDs and self-evaluation
NUREG-1397, NUMARC 90-012, INPO 87-006 and NUREG/CR-5147
Notes: Bottom Line it lead to:
A range of industry regulation and guidance issued as a result of these inspections.
NUREG 1397 and NUMARC 90-012- Design control and design reconstitution\
INPO 87-006 and NUREG/CR-5147 Fundamentals for CM program for Design control

## Slide 8: A Brief History of CM in the Nuclear Industry
Browns Ferry (1985)
Browns Ferry fire in Unit 1 (1975) led to changes in NRC standards for Fire Protection
All three Browns Ferry units shut down voluntarily in March 1985 due to CM related problems - containment isolation testing (Unit 1), reactor water level instrumentation (Unit 2)
Unit 1 restarted in May 2007 after 22 year shutdown
Led to creation of Appendix R to 10CFR50
Notes: Led to creation of Appendix R to 10CFR50
“Train Separation”

## Slide 9: A Brief History of CM in the Nuclear Industry
Nuclear Information and Records Management Association (NIRMA) CM Committee developed solution
  control of technical information by engineering and operations personnel
  mature records management and document control process
PP02-1994 “Position Paper on Configuration Management Program”
NIRMA TG19-1996 “ Configuration Management of Nuclear Facilities”
Basis for ANSI/NIRMA CM-1.0-2000
Notes: In the early ’90s
Mostly focused on control of the Paper.

## Slide 10
CM Equilibrium
Equilibrium Upsets
CM Process Model & Equilibrium Restoration
Using CM to protect Design and Operating Margins
An Individual’s CM Responsibilities
Letting CM get out of Control is Costly
Configuration Management Fundamentals

## Slide 11: What is CM?
The integrated processes that control the activities of design, construction, procurement, operations, and maintenance to ensure that the configuration of the facility is established, approved and maintained
The objective of CM is the conformance of the three elements represented by the CM Equilibrium Model
Require-ments
Facility Config Info
Physical Config

## Slide 12: CM Equilibrium
Technical requirements, derived from the licensing process, or contractual that are reflected in the final design.
What Needs to be there
Licensing characteristics and parameters, referred to as the Licensing Basis, needed for the facility to perform its function
Requirements come from a number of sources; NRC regulations, OSHA, state laws, management direction, design preferences, etc.
For New Builds in particular, Owner Requirements specified in a contract
Requirements
Design Require-ments
Notes: Notice I am not just saying “Nuclear regulations”

## Slide 13: CM Equilibrium
Documentation and Data that define how the plant is designed, operated and maintained.
What we say is there
Design Output Documents and Data; drawings, specifications, calculations, databases, test plans, etc.
Operational Configuration Documents; system alignment checklists, lockout & tagout data, setpoints
Other Operating, Maintenance, Training and Procurement Information; corrective & preventive maintenance, calibration procedures, lesson plans, safeguards SSC information, etc.
Facility Configuration Information
Facility Config Info
Notes: Any of these may be in a database or other electronic format or hard copy

## Slide 14: CM Equilibrium
Actual physical location, arrangement and material condition of Structures, Systems and Components (SSCs)
SSCs as installed (design configuration)
Component position (operating configuration)
SSC Condition – Equipment Reliability
SSCs include a component’s electrical, chemical, and mechanical properties, liquids & coatings, and computer hardware & software
What is actually there
Physical Configuration
Physical Config

## Slide 15: CM Equilibrium
Processes must assure that:
Elements conform all the time
CM Equilibrium is restored in a timely manner if the elements do not conform
All Changes are Evaluated and Approved
People are trained and qualified
Equilibrium conformance can be verified
Require-ments
Facility Config Info
Physical Config

## Slide 16: CM Equilibrium
Processes are the administrative and management measures used to ensure the configuration is maintained. These processes include;
design control
document control
work management
operability, functionality
surveillance & test programs
work protection isolation
formal training and certification
assessments
Require-ments
Facility Config Info
Physical Config

## Slide 17: Identifying and Restoring CM Upsets

## Slide 18
CM Equilibrium Upsets
Upsets are discrepancies within any one of the three elements or between any of the elements.
The following slides provide further explanations and examples
Require-ments
Facility Config Info
Physical Config

## Slide 19
Upsets within any of the three Elements
The design basis of an SSC is often described in multiple places in the FSAR and could be in conflict.
A drawing and an operating procedure may be in conflict
A label on a component my not be updated after the component was changed with a different component type.
CM Equilibrium Upsets
Require-ments
Facility Config Info
Physical Config

## Slide 20
Upsets Between Design Requirements & Facility Configuration Information
Equipment Specifications are less conservative than FSAR Design Basis values
A test requirement in the FSAR is not included in the Plant Test Program
Operating procedure conflicts with a setpoint in the Tech Specs
A procedure conflicts with OSHA personnel safety requirements.
Require-ments
Facility Config Info
CM Equilibrium Upsets

## Slide 21
Examples
FSAR assumes a system can be considered operable provided an operator checks the component once per shift. Operations cost-cutting move changed rounds to once per day.
A modification is installed that puts in a new design pump, but affected preventive maintenance plans were not updated
Management commits to a later code edition and the requirements don’t get flowed down to all required documents
CM Equilibrium Upsets
Require-ments
Facility Config Info

## Slide 22
Upsets Between Physical Config & Facility Configuration Information
The most common CM Equilibrium Upset
Drawing to plant discrepancies
“Midnight Mods” The drawing may not be wrong!
Maintenance uses out of calibration test equipment that invalidates test
Vendor Notice specifying a new lubrication requirement is not implemented in plant
An overgrown tree is removed with a bald eagles nest in a protected area. The tree is shown on the site plan with a note not to remove.
Facility Config Info
Physical Config
CM Equilibrium Upsets

## Slide 23
Upsets Between Design Requirements & Physical Configuration
Failure of SSC to meet design performance criteria specified in an Inservice Test Procedure
Equipment exceeds allowable limits in a Tech Spec
Unexpected degradation in SSC performance
During a system flush, effluent discharge exceeds EPA Permit Limits
CM Equilibrium Upsets
Design Require-ments
Physical Config
Notes: As plant components age or break they may not meet performance requirements that were assumed in the original design.
This is why we constantly monitor their condition and performance using established programs, such as:
field walkdowns, operator rounds, component testing, performance monitoring, erosion & corrosion monitoring

## Slide 24
Examples
Design calculation assumes that an operator can reach a valve to manually close it in 10 minutes. A seismic upgrade included a new load-bearing wall creating an obstacle to access the valve (i.e., increased time to close the valve).
Erosion or corrosion of piping systems exceeds ASME Code limits committed to in the FSAR.
Design Require-ments
Physical Config
CM Equilibrium Upsets

## Slide 25: CM Equilibrium Restoration
The following slides present a high level model using integrated processes to return CM Upsets to Equilibrium
The Process starts with a discrepancy found and recorded in the Corrective Action Program or a desire to change the plant to improve performance.
The question protocol addresses the 3 CM elements

## Slide 26: CM Equilibrium Restoration
CM Equilibrium-The Desired End State
SSCs performing as expected
People are being trained
Procedures are in place and being followed
CM Program is being monitored/trended
Evaluate Identified Problem or Desired Change
Change Facility
Configuration Information ?
Change
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 27: CM Equilibrium Restoration
Evaluate Identified Problem or Desired Change
Apparent discrepancy (discovered error)
Unsatisfactory test results
Desired change (modification, Equivalency Evaluation, manipulating SSCs)
Evaluate Identified Problem or Desired Change
Change
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 28: CM Equilibrium Restoration
Implementing Documents
Evaluate Identified Problem or Desired Change
Problem Identified through Self Assessment Program, System Health Monitoring Program, Periodic Test and Surveillance programs, etc.
Problem Evaluated in Corrective Action Program, Engineering Change Request, Work Request, etc.
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 29: CM Equilibrium Restoration
Change Requirements?
Is a Licensing Requirements impacted? Do I want to accept the condition and change the Requirement?
Does a change affect an Owner (contract) Requirement? Do I want to negotiate a change to the Contract?
Evaluate Identified Problem or Desired Change
Change
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 30: CM Equilibrium Restoration
Implementing Documents
Evaluate impact on Requirements
Processes to evaluate impact of a Requirement include
  Operability (do I have to enter a Limited Condition of Operation until requirement discrepancy is resolved?),
  10CFR50.59 Process (do I have to notify the NRC if I change the requirement),
  FSAR Revision or License Amendment Procedure (the process to change the requirement in the Licensing Basis).
For Contracts, enter contract change process
Requirements Change Process
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 31: CM Equilibrium Restoration
Change Physical Configuration?
Modify SSCs or change position of components?
Use Work Control Process to repair a degraded SSC.
Use Engineering Change Process to change Configuration
Evaluate Identified Problem or Desired Change
Change
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 32: CM Equilibrium Restoration
Implementing Documents
Physical Configuration Change Authorization Process
Design Change Procedure, Equivalency Change Procedure, Temp Mods Procedure, Work Control Procedure, Conduct of Operations Procedure, etc.
Physical Configuration Change Authorization Process
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 33: CM Equilibrium Restoration
Change Facility Configuration Information?
Design Output documents (drawings, calcs, specs, etc.)
Operational configuration documents
Other operating, maintenance, training, etc. documents
“The job is not complete until the paperwork is done”
Evaluate Identified Problem or Desired Change
Change
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 34: CM Equilibrium Restoration
Implementing Documents
Facility Configuration Information Change Process
Drawing update procedure, procedure update procedure, database update procedure, SAR update procedure, maintenance procedure on documenting work package completion, etc.
NOTE: Changing a document only may still require an Engineering Change if the design requirements of an SSC are changed.
Facility Configuration
Information Change Process
33
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 35: CM Equilibrium Restoration
Do Nothing More
Finally a decision may be made to “Use As Is”
Document your conclusion in an appropriate document !
Evaluate Identified Problem or Desired Change
Change
Requirements ?
Change Physical Configuration ?
Do Nothing More
CM Equilibrium
Physical Configuration Change Authorization Process
Requirements Change Process
Facility
Configuration Information Change Process
No
No
Yes
Yes
Yes
No
Change Facility
Configuration Information ?
Notes: This is the point in the CM cycle where the CM Equilibrium has been established.
The Equilibrium may be at the plant level or system level or individual component level.
This condition remains until a problem is identified or an intentional change is considered.

## Slide 36: Margin Management

## Slide 37
Margin is simply additional capability added to an SSC to prevent failure due to wear and tear, or adding additional load. The additional capability is broken into:
  Analytical Margin – The margin that is required to meet your licensing basis imposed by codes and standards
  Design Margin - Additional conservatism added during EPC for unanticipated conditions or later adding new loads.
  Operating Margin - The band of normal events and events of moderate frequency
Using CM to Protect
Design and Operating Margins

## Slide 38: CM EquilibriumMargins
Protect the Design Basis
Design Basis
Each boundary has margins to protect these limits
Design Configuration
Operational Configuration
Operational Configuration conforms to Design Configuration
Design Configuration conforms to Design Basis
Notes: AD-EG-ALL-1106
Attachment 4 (INPO AP 929, Revision 1 Figure C-1)

## Slide 39: Margins
Range of Normal Operation
Ultimate Capability
Operating Margin
Design Margin
Analyzed Design Limit
Operating Limit
Analytical Margin
Documented on design documents
Current Licensing Basis in Design Documents and FSAR
Failure Point Undetermined depends on many variables
controlled by Operations
controlled by Engineering
controlled by License
Notes on Model
describes one parameter only; different parameters may be interrelated
doesn’t represent all possible limits and setpoints
gaps not intended to represent relative size of margins – may be zero

## Slide 40: Margins
Range of Normal Operation
Ultimate Capability
Operating Margin
Design Margin
Analyzed Design Limit
Operating Limit
Analytical Margin
controlled by Operations
controlled by Engineering
controlled by License
Other Limits and Setpoints
Operator Alarm (HI-HI)
Operator Alarm (HI)
SSC Operability is Challenged
Tech Spec Limits

## Slide 41
An Individual’s CM Responsibilities
Performing routine activities in a manner to achieve CM Program objectives and principles. Ensure conformance of the licensing basis requirements with plant information and the physical plant.
Ensuring that changes made to configuration documents are reflected in other affected documents.
Identifying configuration discrepancies through established corrective action processes.
Providing missing information found/developed during research to the appropriate data owner for verification and entry.

## Slide 42
  MILLSTONE NPP SHUTDOWN (early 1996)
  The Plant Had Been Routinely Off-Loading a Full Core During Refueling
  Unfortunately, this Was Not in Their License and NRC Had Not Approved the Maneuver
  More Unfortunately, a Whistleblower Had Been
  Unsuccessful at Convincing Utility Management
  and the NRC That There Was an Issue
  Until He Took His Story to Time Magazine
  Facing Extreme Political and Public Pressure,
  the NRC Shut All 3 Units Down for over a year
  NRC Subsequently Issued the Infamous 10CFR50.54(f) Letter to All Utilities to reassure the NRC under oath that your plant was operating in accordance with Licensing Basis – A BIG DEAL
Early Indicators That CM Was Not Being Applied

## Slide 43: The Impact to the Utility from this Event?
  Unit 1 Shut Down Permanently
  Unit 2 and 3 Were Shut Down for Over
  Two and a Half Years
  The Northeast Utilities Stock Price Dropped From about $25 per Share to about $7
  The Utility was Fined $10M
  Billions of Dollars in Lost Revenues and Recovery Costs
  Utility Eventually Sold Units

## Slide 44: Configuration Management ANSI Standard
ANSI/NIRMA
CM 1.0-2007

## Slide 45: INPO Configuration Management Process Description
AP-929
Notes: Given the Efficiency Bulletin 16-08 eliminated the formal margin mgmt. program as part of DNP along with INPO AP-929 being revised, there is a reason to modify this PPT to reflect those changes?
INPO still expects no margin related SSC reliability issues by relying on Plant Health and CAP processes. At this time (5-1-17) the INPO AP-929 rev 2 is not out yet.

## Slide 46: EPRI Guideline for CM on New Builds
TR 1022684

## Slide 47: Advice from a Long Term CM Practioner
Thoroughly understand the fundamental processes that “preserve” CM
  Engineering Change
  Operability
  Licensing Change
  Work Control
Be the expert in the Station Licensing Basis and know where to go to find it (it won’t be in one place)
Decisions are made on data. Know where to find it. Understand what data is validated and what isn’t. Ensure there is a way to know the difference and that when it is validated there is a simple way to change status.
Avoid the “wow” factor with some of the new tools coming out. Tools are important, understanding the information that the tool manages is much more important
Self Assess Conformance. Review Corrective Action Regularly for CM Issues
Educate, not just Engineering, but the entire station. They all affect CM

## Slide 48
“It’s what you do now
When you don’t have to do anything
That let’s you be
What you want to be
When it’s too late to do anything
about it.”
Warren Owen, former Exec. VP Duke Power

## Slide 49
Вопросы?
Kérdések?
Otázka?
питатння?
Întrebări?
Postavljanje vprašanj?
Klausimai?
Bыnpocu
Pyetje?
Questions?
¿Pregunta?
问题
문제
Հարց
सवाल
سوالات
Notes: This slide show or slightly different earlier versions have been presented at IAEA workshops in Korea, China, Russia, Ukraine, Czech Republic, Hungary and Argentina. “Questions” has been translate into language of those who have attended . Translations may not be accurate.
  Pyetje? Albanian
  Հարց Armenian “haags”
  Bыnpocu Bulgarian “vŭpros”
  问题 Chinese “Wèntí”
  Otázka? Czech
  Kérdések? Hungarian
  सवाल Indian (Hindi) “Selbat”
  문제 Korean “munje”
  Klausimai? Lithuanian “klausimas”
  سوالات Pakistan (Urdu)
  Întrebări? Romanian “intrabaree”
  Вопросы? Russian “vopros”
  Postavljanje vprašanj? Slovenian
  ¿Pregunta? Spanish
  Питатння? Ukrainian “pytannya”