## Slide 1: Palo Verde FLEX Modifications
1
Presented by:
Gene Eimar, Shift Manager - Retired

## Slide 2
Presentation Topics
Primary Plant Modifications
Secondary Plant Modifications
Spent Fuel Pool Cooling Modifications
Electrical System Modifications
2

## Slide 3
3
PRIMARY PLANT MODIFICATIONS

## Slide 4
M
M
M
M
M
M
M
M
RWT
M
M
M
M
HPSI “A”
HPSI “B”
2A COLD LEG
2B COLD LEG
1A COLD LEG
1B COLD LEG
CH “A”
Primary RCS Makeup Connections
4

## Slide 5
M
M
M
M
M
M
M
M
RWT
M
M
M
M
HPSI “A”
HPSI “B”
2A COLD LEG
2B COLD LEG
1A COLD LEG
1B COLD LEG
CH “A”
Alternate RCS Makeup Connections
5

## Slide 6
6
Hydra-Cell Positive Displacement Pump
Max capability = 37 gpm @ 1200 psi @ 1150 RPM
Baldor 480 VAC, 3 phase, 30 HP Motor
Variable Frequency Drive to control RPM
Pump, Motor, suction and discharge hoses contained on trailer.
FLEX RCS Makeup Pump

## Slide 7
7
Secondary Plant Modifications

## Slide 8: Primary SG Feed Connections
CST
RMWT
SG #1
SG #2
M
M
M
M
M
M
M
M
8
AUX FW “A”
AUX FW “B”

## Slide 9: Alternate SG Feed Connections
CST
RMWT
SG #1
M
M
M
M
M
M
M
M
AUX FW “A”
AUX FW “B”
SG #2
9

## Slide 10
10
FLEX SG Feed Pump
Pump Model – Godwin
Engine – John Deere
  225HP @ 2200 RPM
McCrometer 4” flow meter
370 gpm @ 340 psi

## Slide 11
Spent Fuel Pool Cooling
11

## Slide 12
RWT
SFP
FLEX SFP Makeup Paths – Upper Modes
12

## Slide 13
CST
RMWT
AUX FW “A”
AUX FW “B”
SFP
*100 hours after shutdown
FLEX SFP Makeup Paths – Lower Modes
13

## Slide 14
14
FLEX SFP Makeup Pump
Pump Model – Godwin
Engine – John Deere
  156HP @ 2200 RPM
McCrometer 4” flow meter
300 gpm @ 165 psi

## Slide 15
15
Electrical Modifications
  480 VAC Connections
  4160 VAC Connections
  RCS Makeup Pump

## Slide 16
4160 SWITCHGEAR
ESF Transformer
480VAC Load Center
Electrical Alignment
16
480VAC Load Center
480VAC Load Center

## Slide 17
480VAC Load Center
480VAC Load Center
480VAC Load Center
FLEX 480VAC DG
FLEX 480VAC DG
480 VAC Electrical Alignment
17

## Slide 18
18
480 VAC Generator

## Slide 19
FLEX 4160 VAC
Turbine
Generator
4160 SWITCHGEAR
Manual Transfer Switch
ESF Transformer
Alternate Electrical Alignment
19

## Slide 20
20
4160 VAC Bus Connection Box

## Slide 21
21
4160 VAC Manual Switch

## Slide 22
4160 VAC Manual Switch
22
ESF Transformer Position

## Slide 23
4160 VAC Manual Switch
23
Portable Generator Position

## Slide 24
480VAC Load Center
480VAC MCC
FLEX RCS Alternate Pump
FLEX RCS Primary Pump
  RCS Makeup Pump Electrical Connections
24

## Slide 25
FLEX Staging Areas
25
Protected Area Boundary
RCA Yard
CNMT
BLDG
FUEL BLDG
TURBINE BLDG
RW BLDG
CONT BLDG
SERV BLDG
DG BLDG
CST
RWT
PLANT NORTH
“A” SPRAY POND
“B” SPRAY POND
FLEX RCS M/U
FLEX SG Feed
FLEX SFP M/U
FLEX GENERATORS
AUX BLDG

## Slide 26
Presentation Topics
Primary Plant Modifications
Secondary Plant Modifications
Spent Fuel Pool Cooling Modifications
Electrical System Modifications
26

## Slide 27
Questions?
27