## Slide 1
Configuration Management Benchmarking Group
Configuration Management Breakdown:
The Hatch Unit 1 SCRAM and the Path to
Fleet-Wide Digital Configuration Control
What the event revealed about systemic CM gaps, and how Southern Nuclear is responding
Andrew Neal, Lead Engineer | Configuration Management Benchmarking Group | July 2026
CMBG 2026

## Slide 2
The Event in 60 Seconds
A single network switch replacement, performed per accepted practice, triggered an automatic reactor SCRAM — the technical facts set the stage for the CM conversation that follows.
1
Trigger
Switch S28A Replaced
Switch S28A replaced after internal power supply failure on Hatch Unit 1 EX2100/Mark VI network. [1]
STP not enabled on replacement
2
Cascade
Network Data Storm
Within 45 minutes, a network data storm overwhelmed the Unit Data Highway (UDH) and Plant Data Highway (PDH). Mark VI logged over 100,000 entries in 45 minutes with controller communication failures. [1]
3
Consequence
Automatic SCRAM
Turbine control valves (TCVs) drove closed in fail-safe response to corrupted data inputs, driving reactor pressure high and triggering an automatic SCRAM. [1]
Automatic reactor trip
4
Outcome
Controlled Response
Reactor responded as designed. Turbine manually tripped shortly after SCRAM. Plant brought to safe, stable condition — safety systems performed as intended.
Plant stabilized — no safety impact
Andrew Neal, Lead Engineer | Configuration Management Benchmarking Group | July 2026
02

## Slide 3
Root Cause — The Missing Protocol
The Spanning Tree Protocol was not enabled on the replacement switch (existing plant configuration was not properly translated to the replacement switch)
STP Defined
Spanning Tree Protocol
Prevents network loops in redundant Ethernet topologies by blocking duplicate data paths between switches. [1]
Without STP, a redundant crosstie creates an uncontrolled network loop
Original
Switch S28A (failed unit)
STP Status: Enabled — confirmed after temporarily repairing its failed power supply post-event [1]
Loop prevention active through S28A crosstie
Network loop blocked — normal operation
Replacement
Switch S28A (installed unit)
STP Status: NOT enabled — network loop allowed to form through S28A
Processor usage: 88% under loop conditions → dropped to 60% after enabling Rapid STP on the newly installed switch [1]
Mismatch present at installation — no verification step caught it
Critical finding: The configuration mismatch existed from the moment the replacement switch was installed. The central question is not why STP was missing — it is why no verification step caught it.
Hatch Unit 1 SCRAM Root Cause Analysis
3
Note: SNC personnel recognized the STP was not enabled. This was challenged with the Vendor and based on Vendor recommendation and configuration setting sheet, site personnel did not change the setting.

## Slide 4
The Verification That Wasn't
The configuration export tool, for an Allied Tylesyne network switch, always reports STP as disabled — a known-flawed output that was treated as authoritative, providing false assurance of a correct configuration.
Verification Chain: S28A Replacement
Switch S28A Replaced
After internal power supply failure on EX2100/Mark VI network
START
Configuration Printouts Collected
From S28A and other network switches for peer-check comparison [1]
All Printouts Show STP Disabled
Including switches confirmed to be operating correctly
FLAW
Peer-Check Against Flawed Printout
Latent errors introduced by the equipment's own inaccurate export function [1]
FAIL
Verification Accepted as Correct
STP mismatch undetected — installation proceeds
FALSE ✓
Root Findings
Export Tool Always Shows STP Disabled
Configuration exports from these switches will ALWAYS show STP as disabled, regardless of actual runtime state [1]
Unknown Limitation, Undocumented in Procedure
The export tool limitation was not known to personnel performing the work and not addressed in any procedure
Runtime STP Status Requires Web Interface
Actual runtime STP status can only be confirmed via each switch's configuration webpage/interface [1]
The method used for verification was fundamentally incapable of detecting the deficiency — this is a systemic CM gap, not a human error
Andrew Neal, Lead Engineer | Configuration Management Benchmarking Group | July 2026
04 / 12

## Slide 5
Systemic CM Gaps Exposed
The SCRAM was not caused by one mistake — it was permitted by interlocking gaps in configuration management process, procedure, and organizational structure.
1
No Reliable Runtime Verification
No reliable means to verify actual runtime configuration of network switches — export files are unreliable by design [1]
2
Verification Relied on Flawed Printouts
Configuration verification relied solely on printout files — a known-flawed method not discovered until after the event [1]
3
Fragmented Configuration File Storage
Configuration files scattered across site-specific and corporate S: drives — no central controlled repository [2]
4
No Multi-Method Verification Procedure
No standing procedure requiring multi-method verification of network switch settings [1]
Andrew Neal, Lead Engineer | Configuration Management Benchmarking Group | July 2026
5
5
Network Switch Should have been replaced
The network switch should have been included in our lifecycle management plan. It should have been replaced earlier instead of it being run to maintenance.

## Slide 6
Gap Deep Dive
No Reliable Verification Method
The Failed Approach
Industry peer-check assumes the comparison document reflects truth — this assumption failed [1]
Configuration exports from S28A, S25A, and other switches ALL showed STP as disabled — including correctly operating switches [1]
Export tool limitation was not documented, not known to personnel, and not addressed in procedure
Personnel peer-checked against a printout containing latent errors introduced by the equipment's own inaccurate export function [1]
The verification method was fundamentally incapable of detecting the deficiency — this is a systemic CM gap, not a human error
Required Corrective Actions
Actual runtime STP status can ONLY be confirmed via each switch's configuration webpage/interface — not via export files [1]
Fleet recommendation: issue a standing order or fleet-wide communication requiring multi-method verification before replacing any switch in a plant network [1]
Add notation to EX2100/Mark VI topology drawings: STP shall be enabled on all associated network switches [1]
Multi-Method Verification Framework
Export file review — comparison document baseline (known limitation: STP always shows disabled)
Web interface verification — authoritative runtime confirmation of STP state before installation
Drawing notation check — EX2100/Mark VI topology drawings to flag STP requirement explicitly
Andrew Neal, Lead Engineer | Configuration Management Benchmarking Group | July 2026
06 / 12

## Slide 7
The Solution — Digital Configuration Management Plan
The Digital Configuration Management Plan establishes the fleet-wide controlled process that was absent when the Hatch event occurred.
Scope of Coverage
CDAs & non-CDAs; safety-related, important-to-power, and non-safety systems; PLCs, large control systems, digital valve controllers, network devices, cyber security boundary isolation devices [2]
Industry Benchmarks
GitHub
Apache SVN
D2
Southern Company Transmission, WEC, Vogtle 3 & 4 [2]
SNC Plan
Andrew Neal, Lead Engineer | Configuration Management Benchmarking Group | July 2026
9 / 12
Purpose: Establish a controlled, fleet-wide process for storing, retrieving, maintaining, and validating software and configuration files [2]
Repository pivot: Moving from fragmented S: drive storage to the D2 document management system, building on Vogtle 3 & 4 experience [2]
Scope: All digital device types across all Southern Nuclear sites — a true fleet-wide standard where none previously existed [2]

## Slide 8
Implementation Roadmap
Two phases move the fleet from fragmented S: drive storage to a verified, centrally managed D2 repository — with Phase 1 underway now.
Phase 1
Through January 2027
Cross-functional Organizational Kickoff
Complete — 06/10/2026 | Maintenance, Engineering, Projects, Cyber Security — all SNC sites
Inventory of Existing Stored Files
In Progress — through 06/30/2026
D2 Storage/Retrieval Testing
07/01–07/31/2026
Draft Fleet-Wide NMP Development
07/01–07/31/2026
Create Digital Peer Team
08/01/2026
Create New D2 Instance
08/07/2026
Issue Fleet-Wide NMP for Review
08/27/2026
Transfer Existing Files to D2
08/31/2026 – 01/29/2027
Minimum 27 TB D2 storage capacity required for Farley, Hatch, and Vogtle 1 & 2
[2]
Phase 2
February 2027 Onward — Steady State
Normal Backups After Maintenance — routine backup capture integrated into post-maintenance workflow for all digital devices
Periodic Restoration Validation — scheduled tests confirming stored configuration files can be retrieved and restored as expected
Ongoing Proficiency Development — continuous training and procedural refinement as fleet experience matures
[2]
Pivoting from S: drive storage to D2 — expanding on Vogtle 3 & 4 experience; benchmarked against GitHub (Southern Co. Transmission), Apache Subversion (WEC)
[2]
Scope: all CDAs and non-CDAs — safety-related, important to power production, and non-safety-related components across all digital device types
[2]
Complete
In Progress
Planned
10 / 12

## Slide 9
Governance Structure and Key Decisions
The plan establishes the organizational accountability that was absent — a digital peer team for execution and an oversight committee for continuous improvement.
Digital Peer Team
Created 08/01/2026 · Bi-weekly (Phase 1)
Members
I&C Chief Engineer
Electrical and I&C Fleet Support Manager
Vogtle 3 & 4 I&C Design Supervisor
Vogtle 1 & 2 I&C Maintenance Representative
Hatch Cyber Security Engineer
Farley Site Design Engineer
2 At-large members
Phase 1 execution — day-to-day implementation and verification
Oversight / Advisory Committee
Quarterly
Members
Engineering and Maintenance CFAMs
Operations Representative
Digital Projects Manager
CDO Director
Engineering Fleet Support Director
Site-level managers across all SNC sites
Strategic oversight — continuous improvement and governance
NMP Procedure Scope (NMP-GM, cross-functional) [2]
Device-specific appendices · Standardized file naming conventions · Storage locations · Treatment of superseded files
Key Procedural Challenges Being Addressed [2]
Roles/responsibilities across organizations · Backup tools (Acronis/Macrium) · Firmware documentation · Backward compatibility of OS versions
Gap Closure — Multi-Method Verification
Requirement for multi-method verification of network switch settings will be embedded in the new NMP procedure — closing the core gap that enabled the Hatch SCRAM.
Andrew Neal, Lead Engineer | Configuration Management Benchmarking Group | July 2026
11

## Slide 10
References
[1] Nework Switch White Paper.docx
[2] Digital Configuration Management Plan R0.docx